## Sheet1
To be completed by Chair | [8 empty] | To be completed by TAG members
90.1-2019 Section | 90.1-2016 Section- if different | Related IECC Section | Subject | Current Minnesota Amend | Description of Change | Safety & Health Value | Cost Impact | Recommendation A - Accept R - Reject AM - Amend or Comments | Recommendation A - Accept R - Reject AM - Amend | TAG Group Consensus | Stake-holder Consensus | Comments
|  |  |  | Y or N |  | N=None, L=Low M=Med, H=High |  |  |  | Y or N | Y or N
MR 1323 | MN Energy Code Rule
1323.0100 | Subpart 2 |  | Scope |  | Modify scope to rephrase from commercial to non-residential buildings, residential buildings more that three stories in height, and historical residential buildings less than three stories in height not classified as IRC-1, IRC-2, IRC-3, or IRC-4. |  |  | AM- GSM Revised language specific to Model Code Section 2 Scope. Criteria for historic buildings, alterations, and change of occupancy handled elsewhere.
1323.0100 | Subpart 3 |  | Additions, alterations, renovations, or repairs |  | Delete amendments and retain model code language similar and found in 5.1.3 exceptions. |  |  | AM-Renumber and modify this section. Add new amendments to include in Model Code Scoping Section 2. Incorporate detailed scoping into Section 4.1.1 Scope, 4.2 Compliance, and 5.1.3 Exceptions to Envelope Alterations.
1323.0100 | Subpart 4 |  | Change of occupancy or use |  | Add language to include historical buildings and preserving historic character. |  |  | AM-Renumber and modify this section. Add new amendments to include in Model Code Scoping Section 2. Incorporate detailed scoping into Section 4.1.1 Scope and 4.2 Compliance.
1323.0100 | Subpart 5 |  | Change in Space Conditioning |  | Modified to include requirements for semi-heated space conversions. |  |  | Repeal. Model code language is more applicable in Section 4.1.1.5
1323.0100 | Subpart 6 |  | Compliance |  | Language modified to exclude residential buildings three stories and fewer in height instead of all residential buildings. |  |  | Repeal and incorporate language into amended model code section 2 Scope.
1323.0100 | Subpart 7 |  | Mixed Occupancy |  | Clarifying exactly which occupancy group portions of mixed occupancy buildings shall comply with MR 1322. |  |  | Repeal and incorporate language into amended model code section 2.6 and 4.1.1.6.
1323.0100 | Subpart 8 |  | Compliance Materials |  | Repeal. This language is incorporated into the Duties and Powers of the Building Official found in Minnesota Rule 1300.0130, Subpart 2. |  |  | Repeal.
1323.0100 | Subpart 9 |  | Already repealed
1323.0100 | Subpart 10 |  | Information on Construction Documents |  | Renumber and incorporate into model code section 4.2.5.1.1 Information on Building Permit Application |  |  | AM- Amended to incorporate these specific submittal requirement items into the application criteria in 4.2.5.1.1.
Chapter 2 | SCOPE
2.2 |  |  | Scoping |  | Modified to exclude IRC-1, IRC-2, IRC-3 and IRC-4 buildings as well as multi-family structures three stories or fewer in height (except historical buildings), manufactured houses, and buildings that don't use electricity or fossil fuels. |  |  | AM-Review Section 2 revised proposal clarifying incorporation of buildings using site generated energy.
Chapter 3 | DEFINITIONS
|  |  | Building Entrance |  | Consider Amending to Clarify |  |  | Reject proposed amendment. Retain model code language.
|  |  | Buidling Exit |  | Removed |  |  | A
|  |  | Building Grounds Lighting |  | Removed |  |  | A
|  |  | Buidling Service |  | Added |  |  | A
|  |  | Building Service Equipment |  | Added |  |  | A
|  |  | Ceiling Fan |  | Added |  |  | A
|  |  | Coefficient of Performance |  | Modified |  |  | A
|  |  | Commissioning |  | Modified |  |  | A
|  |  | Commissioning Provider |  | Added |  |  | A
|  |  | Computer Room Energy |  | Deleted |  |  | A
|  |  | Conductance |  | Deleted |  |  | A
|  |  | Continuous Dimming |  | Added |  |  | A
|  |  | Cooling Design Wet Bulb Temperature |  | Deleted |  |  | A
|  |  | Daylight Area Under Skylights in Multi-story spaces |  | Added |  |  | A
|  |  | Door |  | Modified- Added Sectional garage door |  |  | Discussed amending, but the actual definition of sectional garage door is adequate. Retain model code language as written.
|  |  | Energy Recovery Ratio, Series (SEER) |  | Added |  |  | A
|  |  | Energy Recovery, series |  | Added |  |  | A
|  |  | Equipment |  | Modified- More specific |  |  | A
|  |  | Fan Array |  | Added |  |  | A
|  |  | Fan, Embedded |  | Added |  |  | A
|  |  | Fan Energy Index (FEI) |  | Added |  |  | A
|  |  | Fan Nameplate Electrical Input Power` |  | Added |  |  | A
|  |  | Fan system electrical power |  | Added |  |  | A
|  |  | Fenestration |  | Modified |  |  | A
|  |  | Fixed |  | Deleted |  |  | A
|  |  | Floor Area, Gross- Gross Building Envelope Floor Area |  | Deleted |  |  | A
|  |  | Floor Area, Gross- Gross Semi-Heated Floor Area |  | Deleted |  |  | A
|  |  | Functional Performance Testing |  | Added |  |  | A
|  |  | Gross Conditioned Floor Area |  | Added |  |  | A
|  |  | Humidistatic Controls |  | Modified |  |  | A
|  |  | Metal Framing |  | Added |  |  | A
|  |  | Multi-level Occupancy Sensor |  | Deleted |  |  | A
|  |  | Multiscene control |  | Deleted |  |  | A
|  |  | Non-metal framing |  | Added |  |  | A
|  |  | non-renewable energy |  | Deleted |  |  | A
|  |  | Non-transient |  | Added |  |  | A
|  |  | Occupied Stand-by mode |  | Added |  |  | A
|  |  | Off-mode power consumption |  | Added |  |  | A
|  |  | on-site electricity generation systems |  | Added |  |  | A
|  |  | PEICL |  | Added |  |  | A
|  |  | PEIVL |  | Added |  |  | A
|  |  | PERCL |  | Added |  |  | A
|  |  | PERSTD |  | Added |  |  | A
|  |  | PERVL |  | Added |  |  | A
|  |  | Primary Side-lighted Area |  | Added |  |  | A
|  |  | Process Application |  | Added |  |  | A
|  |  | Power Usage Effectiveness (PUE) |  | Deleted |  |  | A
|  |  | Process Energy |  | Modified |  |  | A
|  |  | Pump System Power |  | Deleted |  |  | A
|  |  | Pump |  | Added |  |  | A
|  |  | Pump- Clean Water Pump |  | Added |  |  | A
|  |  | Pump- End Suction Closed Coupled (ESCC) pump |  | Added |  |  | A
|  |  | Pump- End suction frame-mounted/own-bearnings (ESFM) pump |  | Added |  |  | A
|  |  | Pump- inline pump |  | Added |  |  | A
|  |  | Pump- Radially split, multistage, vertical inline diffuser casing (RSV) pump |  | Added |  |  | A
|  |  | Pump- Submersible turbine (ST) pump |  | Added |  |  | A
|  |  | Sensible Cooling Panel |  | Deleted |  |  | A
|  |  | Service |  | Deleted |  |  | A
|  |  | Service Equipment |  | Deleted |  |  | A
|  |  | Simulation Program |  | Modified |  |  | A
|  |  | Standby Power Mode Consumption |  | Added |  |  | A
|  |  | Unitary cooling equipment |  | Deleted |  |  | A
|  |  | Unitary Air Conditioners |  | Same definition as Unitary Cooling Eq. |  |  | A
|  |  | Verification and Testing Provider |  | Added |  |  | A
|  |  | Vertical Fenestration |  | Modified |  |  | A
Chapter 4
4.1.1.2 |  |  | Additions to Existing Buildings |  | Modified to include defined terms: Additions, and Existing Buildings |  |  | Accept model code.
4.1.1.6 |  |  | Mixed Occupancy Buildings |  | Integrate clarified requirements for mixed occupancy buildings into the model code. |  |  | AM-Modified to clarify treatment of mixed occupancy buildings.
4.1.1.7 |  | C401.3 | Heating of public commercial parking facilities prohibited |  | Carry-over of existing amendment from state statute 216C.20, Subdivision 3. |  |  | AM- Modifed to integrate into Section 4.1.1.7.
4.1.1.8 |  | 1323.0100, Subp 4 | Change of Occupancy |  | Integrate clarified requirements for change of occupancy buildings and parts of buildings into the model code. |  |  | AM- Modifed to integrate into Section 4.1.1.8. Alterations associated with C of O require compliance with the current code.
4.2.1.3 |  | C402.2.1.2 | Compliance Paths- Alterations to Existing Buildings |  | Adding an exception for historical buildings to eliminate requirements for elements deemed historically significant rather than carte blanc exemption. |  |  | AM
4.2.1.5.1.1 |  | 1323.0100, Subp 10 | Information on Bulding Permit Application |  | Incorporate current application documentation requirements into the model code language. |  |  | AM
4.2.5 |  |  | Verification, Testing and Commissioning |  | Modified- Greatly expanded. |  |  | A
Chapter 5
5.1.2 |  | 1323.0100, Subp 5 | Space Conditioning |  | Adding language to require Builidng Official approval to sprinkle a semi-heated building and posted signage for semi-heated buildings. |  |  | AM
5.1.3 |  | 1323.0100, Subp 3 | Envelope Alterations |  | Modify exceptions by: Deleting exception for partial window replacement, Adding exceptions for roof replacement and historical buildings. |  |  | AM
5.2.1 |  |  | Compliance Paths- Requirements for All Compliance Paths |  | Reformatted with no material change. |  |  | A
5.4.3 |  |  | Air Leakage |  | Charging language added to clarify requirements. No material change. |  |  | A
5.4.3.1.1 | 5.4.3.1.3 |  | Whole Building Air Leakage |  | Reformatted and slightly relocated section. Essentially requires a blower door test for buildings with conditioned and semi-conditioned space to ensure an air leakage rate of 0.40 cfm/ft2 or less. Exception allows an air leakage rate of up to 0.60 0.40 cfm/ft2 with tracing and strategic sealing...no follow up test. Deleted the design option of just providing air resistant materials and not dealing with the connections. |  |  | A
5.4.3.1.2 | 5.4.3.1 |  | Continuous Air Barrier Design and Installation |  | Refomatted with no material change. |  |  | A
5.4.3.3 |  |  | Vestibules and Revolving Doors |  | Reformatted with no material change for our climate zones. Note: The definition of Building Entrance is different than the IECC and results in a more restrictive application than IECC. |  |  | AM- Amend to delete exceptions from this section and relocate them to 5.4.3.3.1
5.4.3.3.1 |  |  | Vestibule Locations |  | Amend to clarify vestibule requirements and relocate exceptions from 5.4.3.3 to 5.4.3.3.1 |  |  | AM- Modify language to clarify where vestibules are required. Relocate exceptions from 5.4.3.3 to here for clarity.
5.4.3.3.2 |  |  | Vestibule Size |  | New section introduces size (area) limits and configuration so that doors are not required to be opened at the same time. |  |  | A
5.5.1 |  |  | Exerior Building Envelope |  | Modified to include a requirement that the exterior surfaces of a conditioned vestibule shall comply with the building envelope requriements of a conditioned space. |  |  | A
5.5.3.1 |  |  | Roof Insulation (Curbs) |  | Language revised to requried minimum R-10 at skylight curbs and other roof curbs. |  |  | AM
5.5.3.2 |  |  | Above Grade Wall Insulation |  | Eliminating non-applicable conditions and requiring that buidling wall insulation shall be either exterior or integral to the wall and not on the interior side. |  |  | AM
5.5.3.3 |  |  | Below Grade Wall Insulation |  | Adding language to require insulation to either be located on the exterior side of the wall or integral to the wall, eliminating the option for interior insulation. |  |  | AM
5.5.3.5 |  |  | Slab-on-Grade Floor Insulation |  | Adding language to require insulation to be located on the exterior side of the foundation. Adding requirement for minimum R-5 continuous insulation under slabs at conditioned spaces. |  |  | AM
5.7 |  |  | Submittals |  | Substantially reformatted into requirements for plan review (permit application) and closeout (Completion). Permit application requirements are materially the same. Completion requirements are new. |  |  | A
5.8.1.2 Exception |  |  | Mfg Installation Instr. |  | Modified to clarify requirements for pre-engineered metal building insulation installation. |  |  | A
5.8.1.11 |  |  | Insulation Installation Documentation |  | New section added to require an affidavit from the installer certifying that the insulation was installed in accordance with its listing. |  |  | A
5.8.2.5 |  |  | Exception Added |  | Exception criteria added for tubular daylighting devices. |  |  | A
5.8.3 |  |  | Air Leakage |  | New section |  |  | A
5.9.1 | 5.9.2 |  | Building Envelope Performance Verification |  | Relocated section |  |  | A
5.9.2 |  |  | Commissioning |  | New: Commisssioning of the building envelope now required with report provided. |  |  | A
6.1.1.3.6 |  |  | Alterations to Existing Buildings- Rooftop HVACR |  | Add section to require curb replacement when rooftop equipment is changed and the existing roof curbs do not permit installation of roof insulation to current code requried thicknesses. |  |  | AM
6.2.1 |  |  | Requirements for all compliance paths |  | Modified for clarity with no material change. Parts of the previous version's section migrated to 6.2.2. |  |  | A
6.2.2 |  |  | Additional Requirements to comply with Section 6 |  | Deleted referece to Energy Cost Budget Method in Section 11. Modified to expand on the previous version's section 6.2.1 to provide more clarity. |  |  | AM
|  |  | Exception 6.2.2(a) |  | Added as part of modification ot 6.2.1, no material change. |  |  | A
|  |  | Exception 6.2.2(b) |  | New exception in this section for HVAC systems serving computer rooms > 10KW of equipment power. |  |  | A
6.3.2 |  |  | Simplified Approach Criteria |  | Item r: added compliance with occupied-standby controls in Section 6.5.3.8. |  |  | A
6.4.1.1 |  |  | Mandatory Provisions- Minimum Equipment Efficiences |  | Expanded section scoping range from (6.8.1-1 through 6.8.1-16) to (6.8.1-1 through 6.8.1-20) |  |  | A
|  |  | Item h Deleted |  | Deleted: "Table 6.8.1-8 Heat transfer equipment" |  |  | A
|  |  | Item h Relocated |  | Relocated from Item J |  |  | A
|  |  | Item I Modified |  | Added: Applied Heat Pumps to combine Item I with previous Item j. |  |  | A
|  |  | Item j |  | Moved to Item h. |  |  | A
|  |  | Item j |  | Previously Item k: Modified to specifically address floor mounted air conditioners. |  |  | A
|  |  | Item K |  | Relocated to Item J |  |  | A
|  |  | Item K |  | Previously Item L: Modified with no material change. |  |  | A
|  |  | Item L |  | Deleted: "Table 6.8.1-12 "commercial refrigerator and freezers minimum efficiency" |  |  | A
|  |  | Item L |  | Relocated from Item N- Vapor compression based indoor pool dehumidifiers. |  |  | A
|  |  | Item m |  | Previous Item m Deleted: "Table 6.8.1-13 Commercial Refrigeration- minimum efficiency requirements" |  |  | A
|  |  | Item m |  | Relocated from Item O |  |  | A
|  |  | Item n |  | Relocated to item L |  |  | A
|  |  | Item n |  | Relocated from item P |  |  | A
|  |  | Item O |  | Relocated to Item m |  |  | A
|  |  | Item O |  | New section: Table 6.8.1-15 Electrically Operated Water-source Heat Pumps- minimum efficiency requirements |  |  | A
|  |  | Item P |  | Relocated to Item n |  |  | A
|  |  | Item P |  | New Section: Table 6.8.1-16Heat Pump and Heat Recovery Chlller packagtes- minimum efficiency requirements |  |  | A
|  |  | Item Q |  | New section: 6.8.1-17 Ceiling mounted computer room air conditioners- minimum efficiency requirements. |  |  | A
|  |  | Item R |  | New Section: Table 6.8.1-18 Walk-in Cooler and Freezer Display Door Efficiency Requirements. |  |  | A
|  |  | Item S |  | New Section: Table 6.8.1-19 Walk-in Cooler and Freezer nondisplay door efficiency requirements |  |  | A
|  |  | Item T |  | New Section: Table 6.8.1-20 Walk-in Cooler and freezer refrigeration system efficiency requirements. |  |  | A
6.4.1.3 |  |  | Ceiling Fans |  | New Section and subsections providing criteria for large diameter ceiling fans |  |  | A
6.4.1.5 |  |  | Verification of Equipment Efficiencies |  | Deleted verification method f: "Requirements for plate-type liquid-to-liquid heat exchangers are listed in Table 6.8.1-8." |  |  | A
6.4.3.3.5.1 |  |  | Guest Room HVAC Set-Point Control |  | Reformatted. Reset time changed to 20 minutes in lieu of 30 minute. Reformatted for clarity with no other material changes. |  |  | A
|  |  | Exception Added |  | Cooling for humidity control shall be permitted during rented and unoccupied or unrented and unoccupied periods. |  |  | A
6.4.3.3.5.2 |  |  | Guest Room Ventilation Control |  | Setback period changed from 30 minutes to 20 minutes. |  |  | A
6.4.3.4.2 Exceptions |  | C403.7.7 | Ventilation System- Shutoff Damper Controls |  | Need to discuss if an exception for buidlings three stories or less in height is acceptable for any size damper. This is most of our buildings. ASHRAE limits this exception to Climate Zone 3 and lower. Consider keeping our exception 2 and adding it to the list in ASHRAE as Exception 6. exhaust ducts 8" and smaller may have spring-loaded backdraft dampers with weather hoods. |  |  | DISCUSS
Table 6.4.3.4.3 |  |  | Maximum Damper Leakage |  | Table modified allowing for nonmotorized dampers where the capacity is 300 cfm or less for outdoor air intake for all buildings and for exhaust/relief on buildings three or more stories in height. |  |  | DISCUSS
6.4.3.6 |  |  | Humidification and dehumidification control |  | Section modified to set the bottom dew point limit for dehumidification at 55F. No other material change. |  |  | A
6.4.4.2.1 |  | C403.11 | Duct Insulation and Sealing |  | MN Amended the IECC related section C403.11 extensively to address sealing requirements for low pressure, medium pressure, and high pressure ductwork. Discuss if this is relavent to move forward into the new code. |  |  | DISCUSS
6.4.5 |  |  | Walk-in Coolers & Freezers |  | Item m added to requriements: Doors shall meet the requirements of Tables 6.8.1-18 and 6.8.1-19. Systems except for walk-in process cooling refrigeration systems as defined in 10 CFR 431.302 shall meet the requriements of Table 6.8.1-20. |  |  | A
6.4.7 |  |  | Liquid-to-liquid Heat Exchangers |  | Section ADDED. Plate exchangers shall be rated according to AHRI 400. |  |  | A
6.5.1.1.4 |  |  | Air Economizer Dampers |  | Return Air dampers requirement modified to comply with 6.4.3.4.3 without specific reference to requirements for motorized dampers only. Non-motorized dampers will now be allowed to meet those requirements. The result is less restrictive. (Air Damper Leakage) |  |  | A
6.5.2.1 |  |  | Exception 1 Zone Controls |  | Deleted: b. The outdoor airflow rate requried to meet the ventilation requirements of ASHRAE Standard 62.1 for the Zone. |  |  | A
6.5.2.1 |  |  | Exception 1 Zone Controls |  | Added: b. For systems with DDC, the minimum primary airflow rate required to meet the Simplified Procedure ventilation requiremetns of ASHRAE Standard 62.1 for the zone, permitted to be the average airflow rate as allowed by ASHRAE Standard 62.1. |  |  | A
6.5.2.1 |  |  | Exception 2 Zone Controls |  | Exception 2 applies to Zones with DDC that comply with all of the following: Deleted: Under Item a- Subitems (1) and (2) are deleted. (1) Twenty perecent of the zone design peak supply rate. (2) The oudoor airflow rate required to meet the ventilation requirements fo ASHRAE Standard 62.1 for the zone. |  |  | A
6.5.2.1 |  |  | Exception 2 Zone Controls |  | Exception 2 applies to Zones with DDC that comply with all of the following: Added: Under Item a is new Subitem (1) The minimum primary airflow rate required to meet the Sipmplified Procedure ventilation requriemetns of ASHRAE Standard 62.1 for the zone, permitted to be the average airflow rate as allowed by ASHRAE Standard 62.1. |  |  | A
6.5.3.1.2 |  |  | Fan Motor Selection |  | Section modified with no material change to the charging language when considered with the first two exceptions of the previous code. Added new exception 1 "Motors equipped with electronic speed control devices to vary the fan airflow as a function of load." And, exception 4 "Fans iwth a fan nameplate electrical input power of less than 0.89 kW. |  |  | A
6.5.3.1.3 |  |  | Fan Efficiency |  | Section modified. Need to review/discuss. Scoping and exceptions changed. |  |  | DISCUSS
6.5.3.5 |  |  | Supply Air Temperature Reset Controls |  | Exceptions 1 thorugh 3 completely rewritten. |  |  | A
6.5.3.5.1 |  |  | Dehumidification Control Interaction |  | New section only applicable to Zones 0A through 3A. |  |  | A
6.5.3.8 |  |  | Occupied-Standby Controls |  | New Section for review. |  |  | DISCUSS
6.5.4.8 |  |  | Buildings with High-Capacity Space-Heating Gas Boiler Systems |  | New section affecting new buildings with boiler capacities between 1,000,000 Btu/h and 10,000,000 Btu/h. Includes new subsections 6.5.4.8.1 Boiler Efficiency and 6.5.4.8.2 Hot-Water Distribution System Design. |  |  | A
6.5.6 |  |  | Exhaust Air Recovery |  | New Sections inserted |  |  | A
6.5.6.1.2 Exception 6 |  |  | Exhaust Air Recovery- Exception 6 Loophole |  | Discuss modifying exception 6 to eliminate the loophole allowing circumventing of energy recovery for nearly every project. |  |  | AM
Tables 6.5.6.1.2-1 and 6.5.6.1.2-2 |  | Table C403.7 | Exhaust Energy Recovery Tables |  | MN Amended previous table. Sonar includes discussion regarding low efficacy at very cold temperatures and outdoor ventilation air < 30%. Discuss modifying the ASHRAE Tables or not. |  |  | DISCUSS
6.5.6.1.1 |  |  | Non-transient dwelling units |  | New section added. Requires energy enthalpy recovery for exhausted heat at efficiencies of 60% or greater. |  |  | A
6.5.6.1.2 |  |  | Other than Non-transient Dwelling Units |  | Modified from previous language found in 6.5.6.1 to include new reference to Table 6.5.6.1.2-1 for ventilation systems operating at more than 8,000 hours per year. (Note: 8760 hours in a year) Discuss major loophole in Exception 6. |  |  | DISCUSS
|  |  | Exceptions modified |  | Exceptions 4 and 5 changed "heating energy recovery" and "cooling energy recovery" to Enthalpy Energy Recovery. Exception 9 added for indoor pool dehumidifiers complaint with Section 6.5.6.4 |  |  | A
6.5.6.3 |  |  | Heat Recovery for Space Conditioning |  | New Section: Specific to only inpatient hospitals in Climate Zone 6A. |  |  | A
6.5.6.4 |  |  | Indoor Pool Dehumidifier Energy Recovery |  | New section requires enthalpy recovery for swimming pool exhaust where the pool is over 500 square feet unless 60% or more of the space conditioning energy is from on-site renewable resources. |  |  | A
6.6.1 |  |  | Alternative Compliance Path- Computer Rooms Systems |  | Section significantly modified and condensed. Application revised to computer rooms with IT equipment loads exceeding 10 kW |  |  | A
Old 6.7.2.4 |  |  | System Commissioning |  | Section relocated to 6.9 and modified. |  |  | A
6.9.1 |  |  | Verification and Testing |  | Section rewritten to cross reference to other sections. Exception for instructions deleted. Cross reference eliminates the requirement for commissioning for buildings under 10,000 sf. 4.2.5.2 Exception 1 |  |  | A
Table 6.8.1-1 |  |  | Electrically Operated Unitary Air Conditioners and Condensing Units |  | Minimum efficiencies generally increased and incrementally increased again as of 1/1/23. |  |  | A
Table 6.8.1-2 |  |  | Electrically Operated Air-Cooled Unitary Heat Pumps |  | Minimum efficiencies generally increased and incrementally increased again as of 1/1/23. |  |  | A
Table 6.8.1-3 |  |  | Water Chilling Packages |  | No Change |  |  | A
Table 6.8.1-4 |  |  | Electrically Operated Packaged Terminal Air Conditioners, Packaged Terminal Heat Pumps, Single-Package Vertical Air Conditioners, Single-Package Vertical Heat Pumps, Room Air Conditioners, and Room Air Conditioner Heat Pumps. |  | Table reconfigured. Review. |  |  | DISCUSS
Table 6.8.1-5 |  |  | Warm-Air Furnaces and Combination Warm Air Furnaces/Air Conditioning Units, Warm Air Duct Furnaces, and Unit Heaters |  | Minimum efficiencies generally increased and some incrementally increased again as of 1/1/23. |  |  | A
Table 6.8.1-6 |  |  | Gas and Oil-Fired Boilers |  | No Change |  |  | A
Table 6.8.1-7 |  |  | Performance Requirements for Heat Rejection Equipment |  | Propeller or axial fan dry coolers (air-cooled fluid coolers) added. Subcategory or rating condition modified for Propeller or Axial Fan evaporative condensers. |  |  | A
Old Table 6.8.1-8 |  |  | Heat Transfer Equipment |  | Table deleted. Note: Section added to narrative. |  |  | A
Table 6.8.1-8 |  |  | Electtrically Operated Variable Refrigerant Flow Air Conditioners |  | No Change |  |  | A
Table 6.8.1-9 |  |  | Electrically Operated Variable Refrigerant Flow and Applied Heat Pumps |  | No Change |  |  | A
Table 6.8.1-10 |  |  | Floor Mounted Air Conditioners and Condensing Units Serving Computer Rooms |  | Table reconfigured. Review. |  |  | A
Table 6.8.1-11 |  |  | Commercial Refrigerators and Freezers |  | Table reconfigured. Review. |  |  | A
Table 6.8.1-12 |  |  | Vapor Compression Based Indoor Pool Dehumidifiers |  | No Change |  |  | A
Table 6.8.1-13 |  |  | Electrically Operated DX-DOAS Units, Single-Package and Remote Condenser, without Energy Recovery |  | No Change |  |  | A
Table 6.8.1-14 |  |  | Electrically Operated DX-DOAS Units, Single-Package and Remote Condenser, with Energy Recovery |  | No Change |  |  | A
Table 6.8.1-15 |  |  | Electrically operated Water-Source Heat Pumps |  | New Table |  |  | A
Table 6.8.1-16 |  |  | Heat-Pump and Heat Recovery Chiller Packages |  | New Table |  |  | A
Table 6.8.1-17 |  |  | Ceiling Mounted Computer Room Air Conditioners |  | New Table |  |  | A
Table 6.8.1-18 |  |  | Walk-In Cooler and Freezer Display Door |  | New Table |  |  | A
Table 6.8.1-19 |  |  | Walk-in Cooler and Freezer- nondisplay door |  | New Table |  |  | A
Table 6.8.1-20 |  |  | Walk-in Cooler and freezer Refrigeration System |  | New Table |  |  | A
Table 6.8.2 |  |  | Minimum Duct Insulation R-value |  | Indirectly conditioned space model code differs from amended IECC. ASHRAE R-1.9, IECC R-3. Amend to keep R-3, or make indirectly conditioned the same as unconditioned? |  |  | DISCUSS
Table 6.8.3-1 |  |  | Minimum Piping Insulation Thickness Heating and hot water systems |  | No Change |  |  | A
Table 6.8.3-2 |  |  | Minimum Piping Insulation Thickness Cooling Systems |  | No Change |  |  | A
Chapter 7 Service Water Heating
7.1.1.3 |  |  | Alterations- Heat Trap |  | Add language to require installation of heat traps when water heaters are replaced, and to insulate exposed hot water piping where it is accessible in proximity to the water heater. |  |  | AM
7.2 |  |  | Compliance Paths |  | Reformatted. No material change |  |  | A
7.7 |  |  | Submittals |  | Section largely expanded rather than referring to Section 4.2.2. No material change. |  |  | A
7.9 |  |  | Verification, Testing, and Commissioning |  | New Section.
Table 7.8 |  |  | Performance Requirements for Water Heating Equipment |  | 1. Added Electric Instantaneous Water Heaters. 2. Performance requirements modified and metric changed. Need to discuss if this is a material change or not. |  |  | Discuss
Chapter 8 Power
8.2.1 Exception |  |  | Requirements for all compliance paths |  | Exception added for power distribution systems and equipment serving only computer rooms with > 10kW IT Loads.
8.4.2 |  |  | Automatic Receptacle Control |  | This expensive requirement is frequently and readily circumvented with extension cords introducing a more dangerous condition. May no longer be necessary with sub-metering requirements for outlets and some additional education of building occupants. |  |  | AM to Delete. Discuss.
8.61 |  |  | Alternative Compliance Path- Computer Rooms |  | New section added specific to computer rooms with IT power load greater than 10 kW. |  |  | A
8.9 |  |  | Verification, Testing, and Commissioning |  | New section. |  |  | A
Chapter 9 Lighting
9.1.4 |  |  | Interior and Exterior Luminaire Wattage |  | Add item e regarding DC low voltage lighting systems with flexible cabling. Review. |  |  | Discuss
9.2 |  |  | Compliance Paths |  | Section and subsections rewritten. Modified to include a "Simplified Building Method Compliance Path." |  |  | A
9.2.3.2 |  |  | Exterior Lighting Power Allowance |  | New section added to compliance paths. |  |  | A
Table 9.2.3.1 |  |  | Table of Exceptions to Interior Lighting Power and Minimum control requirements |  | New table corresponding to 9.2.2.3 Exceptions. Added variations to required controls for many of the exceptions. |  |  | A
9.3 |  |  | Simplified Building Method Compliance Path |  | New section added as an option to the other compliance paths. The option of using this table is slightly more restrictive than the Building Area Method. |  |  | A
9.4.1.1 e |  |  | Mandatory Interior Lighting Controls |  | Item e Modified charactoristics 2 & 3 to require continuous dimming in daylight areas down to 20% and Item 3 now includes requirements for dimming in daylight areas that also have occupancy sensors such that the dimming modulates only to the limits of the unoccupied threshold when the space is unoccupied. |  |  | A
|  |  | Exception 4 added |  | New exception for primarily side-lighted areas adjacent to vertical fenestration where there are qualifying external projections that function as shading devices to block direct sunlight. |  |  | A
|  |  | Item F: |  | Significanly modified the requriements for top-lighting daylighting. Similary to side-lighting, dimming shall be down to 20%, Calibration shall be not higher than 11 feet, and the dimming shall be limited by unoccupied thresholds when the space is unoccupied. |  |  | A
|  |  | Item j: |  | New Item for scheduled off during non-business hours. |  |  | A
9.4.1.2 |  |  | Parking Garage Lighting Control |  | 1) Lighting power reduction to 50% within 10 minutes of no activity in lieu of 30% reduction after 20 minutes. 2) Daylighting transition area must go to the general lighting level of the garage from sunset to sunrise in lieu of just a reduced power level for this brighter area, 3) Daylighting controls for the garage lighting come into play at 24 square feet of wall opening in lieu of 40% of the exterior wall area open. Added exceptions to daylighting requirements. |  |  | A
9.4.1.3 |  |  | Special Applications Lighting |  | Reformattted. No material change. |  |  | A
Table 9.4.2-2 |  |  | Individual Lighting Power Allowances for Building Exteriors |  | Loading dock allowance adjusted down to 0.2 W/SF in Zones 2, 3, and 4. Outdoor sales areas not fronting on a street reduced to 0.2 W/SF in zones 3 and 4. Added section for areas not included elsewhere in the table. |  |  | A
9.4.3 |  |  | Funcitonal Testing |  | Deleted |  |  | A
9.4.3 |  |  | Dwelling Units |  | Renumbered section, adding an exception clarifying that hotel/motel guest rooms have requirements in Table 9.6.1 and Section 9.4.1.3(b) |  |  | A
Table 9.5.1 |  |  | Lighting Power Density Allowances- Building Area Method |  | Every allowance changed, most down. |  |  | A
Table 9.6.1 |  |  | Lighting Power Density Allowances- Space by Space Method |  | Nearly every allowance changed, most down. |  |  | A
9.9 |  |  | Verification, Testing, and Commissioning |  | New Section. |  |  | A
Chapter 10 Other Equipment
10.4.5 |  |  | Air Curtains |  | New Section |  |  | A
10.4.7 |  |  | Pumps |  | New Section |  |  | A
10.7 |  |  | Submittals |  | New Section |  |  | A
10.9 |  |  | Verification, Testing, and Commissioning |  | New Section |  |  | A
Table 10.8-6 |  |  | Maximum Pump Energy Index (PEI) |  | New Table |  |  | A
Chapter 11 Energy Cost Budget Method
11.2 |  |  | Compliance |  | Added compliance requirements d) Verification, Testing & Commissioning, and e) Proposed components and systems without critieria in the prescriptive requirements shall have verification or testing do document proper installation & operation. |  |  | A
11.4.1 |  |  | Simulation Program |  | Scope modified to include a direct reference to Section 11.4.5 Exceptional Calculation Methods when components can't be modeled by the simulation. |  |  | A
11.4.1.1a |  |  | Simulation Program |  | Changed modeling hours from minimum of 1400 hours per year to 8700 hours per year. Note: 8760 hours in a year. |  |  | A
11.4.1.4 |  |  | Simulation Program |  | Test results reporting criteria added. |  |  | A
11.4.2 |  |  | Climatic Data |  | Added to the data under consideration/study includes solar radiation, wind speed, wind direction. |  |  | A
11.4.3.1 |  |  | On-site renewable Energy |  | Expands the options available for including on-site renewables that are leased in part or in whole, and includes limits on energy cost offsets. |  |  | A
11.4.3.2 |  |  | Annual Energy Costs |  | Added language to include guidance regarding on-site electricity generation from other than renewable resources and how to incorporate that into the calculation. (Co-generation) |  |  | A
11.4.5 |  |  | Exceptional Calculation Methods |  | Section substantially reconfigured and modified with no material change. Instructions give better guidance for more specific submittal requirements. |  |  | A
11.5.1 |  |  | Calculation of Design Energy Cost and Energy Cost Budget |  | Exception added to exclude energy used to recharge vehicles for off-site transportation. |  |  | A
11.5.2 c |  |  | HVAC- Supply Fan Energy In Package Equipment |  | Section expanded to provide guidance where multiple HVAC zones are combined into a single thermal block. Limits Q to 760,000 Btu/h. |  |  | A
11.5.2 d |  |  | Minimum Outdoor Air Ventilation Rate Exceptions |  | Two exceptions added |  |  | A
11.5.2 g |  |  | HVAC- Supply Air Flow Rates |  | Clarification for relaxing set-point requirements to a maximum 20 degree differential |  |  | A
11.5.2 g |  |  | Exceptions |  | Two exceptions added |  |  | A
11.7.2 |  |  | Permit Application Documentation |  | Many additional requirements. New are items b, c, e, f, g, h, I, k, m, and o. |  |  | A
Table 11.5.1, Item 3 |  |  | Space Use Classification |  | Exception added to clarify procedure when space types do not exist or are not designated in the design documents. |  |  | A
Table 11.5.1, Item 4 |  |  | Schedules |  | Temperature and Humidity Schedules as well as HVAC Fan Schedules and exceptions added. |  |  | A
Table 11.5.1, Item 5 |  |  | Building Envelope |  | Item d Skylights added to the Budget Building Design. |  |  | A
Table 11.5.1, Item 6 |  |  | Lighting |  | Proposed Design: Item d modified to include supplemental requriemetns for dwelling units and hotel/motel guest rooms. Item f inserted to incorporate the previous exception into affirmative language for clarity, Item g was previously Item f, and is modified for clarity with no material change. |  |  | A
Table 11.5.1, Item 6 |  |  | Lighting |  | Budget Building Design: Item a is new and allows an existing lighting system to be the budget lighting system. Item b adds specificity to dwelling units establishing the lighting power density at 0.60 W/sf. Item c is new providing guidance where there is no lighting design submitted. |  |  | A
Table 11.5.1, Item 7 |  |  | Thermal Blocks |  | Exception Condition 1 modified to consider thermal blocks as similar if they have internal loads within 10 Btu/Ft2 of each other. Condition 4 is added to ensure that similar thermal blocks have load schedules that differ by 40 hours per week or less for full work load. |  |  | A
Table 11.5.1, Item 9 |  |  | Thermal Blocks- Multi-Family Residential |  | Modified for clarity with no material change. "Thermal Blocks" to "HVAC Zones"; "Space" to "Dwelling Unit" |  |  | A
Table 11.5.1, Item 9 |  |  | Proposed Design: Service Water Heating Systems |  | Modified to add the clarification: "Piping losses shall not be modeled." |  |  | A
Table 11.5.1, Item 9 |  |  | Budget Building Design: Service Water Heating Systems |  | Modified to add clarifications: Calculations shall be based upon the volume of service water heating required. Entering water temperatures shall be estimated and leaving water temperatures based on end-use requirements. Piping losses shall not be modeled. |  |  | A
Table 11.5.1, Item 12 |  |  | Proposed Design: Miscellaneous Loads |  | Removed refrigeration equipment from the calculation. Added clarifying subparts a and b pertaining to Power and Other Equipment sections. Where designs are provided, the designs shall comply with Sections 8 and 10 and the designs shall be used (which may be more efficient than requried by Sections 8 or 10). Where no design is submitted, Sections 8 and 10 shall be used as the basis for determining compliance with no increase in efficiency in these areas beyond prescriptive limits. |  |  | A
Table 11.5.1, Item 12 |  |  | Budget Building Design: Miscellaneous Loads |  | Revised to read "Same as proposed design." No material change, except refrigeration equipment is also removed from the calculation. |  |  | A
Table 11.5.1, Item 13 |  |  | Refrigeration |  | New Section Added |  |  | A
Table 11.5.1, Item 14 |  |  | Modeling Exceptions |  | New Section Added |  |  | A
Table 11.5.2-1 |  |  | Budget System Descriptions |  | Footnotes b, d, and e modified. Review. |  |  | A
Table 11.5.2-3 |  |  | Water Chiller Types |  | Electric Chiller Type for capacities 100 Tons and less changed to "Scroll" from "Reciprocating" |  |  | A
Table 11.5.2-5 |  |  | Cooling Tower Leaving Water Temperature |  | New Table- Review |  |  | A