## Sheet1
ASHRAE 90.1-2022 - Addendum for Review
Internal No. | 2022 Addenda | Date Approved | Description | ASHRAE Code Section | Purpose
1 | a | 2023-05-16 | Addendum a modifies Normative Appendix G to address a known issue with how purchased heating and cooling is handled. Prior to adoption of a stable baseline in Appendix G, purchased heating and cooling were treated as energy neutral. With the adoption of a stable baseline and BPF factors, a proposed design using purchased heating and cooling has more difficulty meeting the PCI target. Addendum a addresses this issue by requiring purchased heating and cooling to be modeled in the proposed design as being supplied by a minimally code-compliant hot- and chilled-water plant. |  | Administrative
2 | b | 2023-09-14 | Exterior lighting power section and LPD allowance clarifications. |  | Administrative
3 | c | 2024-08-02 | For systems that automatically changeover between heating and cooling, users often do not know what set point they are adjusting. In some systems, the displayed set point is between the two set points; in others, it is the cooling set point with the heating set point equal to the cooling set point less a dead band that is typically not user adjustable. Either way, when the user adjusts the set point, both heating and cooling move together, maintaining the currently programmed dead band. But if the programmed dead band is set to a low value, such as 1°F (0.5°C), any set-point adjustment more than 1°F (0.5°C) will cause the system to change modes, though that may not be what the occupant intended. A classic example is a hotel room where the housekeeper often turns the set point down to 65°F, then the guest arrives and wants the room to be warmer. By changing the set point to 70°F, the system switches to heating, because the internal dead band is almost always set to a low value. The more efficient operation would be to raise the cooling set point but not the heating set point and allow the space to naturally rise to 70°F without any heating. Another example is set-point adjustment for demand response. When utilities (or local demand limiting logic) indicate a need to reduce demand, cooling set points are adjusted upward while heating set points are adjusted downward; this cannot happen if systems have the two set points tied together, and if they are, raising the cooling set point might push a zone into heating and inadvertently increase electricity demand for systems using electricity for heating. This addendum updates Standard 90.1 as follows: a. Separate set points are now required for heating and cooling, each individually adjusted without one being tied to the other. b. A minimum of 1°F (0.5°C) has been established for the dead band between heating and cooling. c. The exception for occupancies needing tighter control is now only an exception to the dead band configuration value, set to 1°F (0.5°C) instead of 5°F (3°C). There is no reason for these occupancies to not have the capability of separate set points and wider dead band values. Because these occupancies generally use the same control systems as other occupancies, changing this exception will have minimal or no impact on control system hardware and software. d. Where set points are displayed and user adjustable, either both set points must be displayed or the active set point and its mode (heating or cooling) must be displayed. | 6.4.3.1.2 (modify) 6.4.3.1.3 (modify) 6.4.3.2 (modify) | Energy Savings
4 | d | 2023-06-30 | Ground Source Heat Pump systems heat rejection adjustments |  | Energy Savings
5 | f | 2023-06-30 | Updates to modeling requirements for calculating design energy cost and energy cost budget as well as calculating proposed building performance and baseline building performance |  | Energy Savings
6 | h | 2024-03-14 | The addendum’s intent is only to address the potential double counting of efficiency exceptions in Sections 6 and 7 for on-site renewable resources. |  | Administrative
7 | i | 2024-03-14 | Addendum i modifies service water heating energy credit measure W08 |  | Energy Savings
8 | j | 2024-03-14 | Addendum j adds the Mechanical System Performance Rating Method as a more flexible HVAC energy credit measure. This is an alternative to the simplified efficiency measures H02 and H03, and also is an alternative to measure H05 ground source heat pump and measure H06 dedicated outdoor system. H01 reflects the system energy impact of the proposed mechanical system compared to a target system. When the total system performance ratio (TSPR) is greater than the target system, it indicates energy savings. |  | Energy Savings
9 | k | 2024-04-24 | Addendum k defines qualifying off-site sources of renewable energy that can be applied to the renewable energy requirements and under which conditions offsite procurement can be used. |  | Administrative
10 | l | 2024-05-03 | Addendum l adds a new appendix, Informative Appendix M, to Standard 90.1. It is intended to be adopted by jurisdictions or rating authorities wanting to achieve net zero operational energy emissions (NZOEE) buildings with the energy code over one to three code cycles. It does not address emissions associated with other building operations, such as refrigerants or embodied emissions associated with building materials. The method requires using the performance compliance path and meeting two performance metric targets. The Site Performance Energy Index (PEIsite) provides an efficiency backstop. The Greenhouse Gas Performance Emissions Index (PEIco2e) measures zero net operational emissions achievement. |  | Administrative
11 | m | 2024-03-14 | Addendum m adds requirements that hydronic and direct-exchange (DX) fin-and-tube coils be rated according to AHRI 410-2023 (SI/I-P), Performance Rating of Forced-Circulation Air-Cooling and Air-Heating Coils, and exhaust-air energy recovery heat exchangers be rated according to AHRI 1060 (I-P/2018), Performance Rating of Air-to-Air Exchangers for Energy Recovery Ventilation Equipment. The existing rating requirement for liquid-to-liquid heat exchangers remains. Rating to AHRI 400 has resulted in significantly more accurate performance ratings for liquid-to-liquid heat exchangers, which results in systems that are more likely to perform as designed |  | Administrative
12 | n | 2024-04-24 | Addendum n fixes the issue by: - Introducing a new Exception 5 to Section G3.2.2.4 - Eliminating baseline case fan power adjustment for gas-phase air cleaning when applying Exception 5 to Section G3.2.2.4 - Adding a new section, “Air Cleaning” to Table G3.1 to explicitly specify that the baseline-case energy model should not include gas-phase air-cleaning system energy |  | Energy Savings
13 | o | 2024-03-29 | This addendum clarifies the requirements for demand control ventilation when using CO2-based controls based on an update to ASHRAE Standard 62.1. The Standard 90.1 requirement mandating demand control ventilation (DCV) in densely occupied spaces does not specify how DCV is accomplished. ANSI/ASHRAE Standard 62.1-2022 Addendum ab provides very specific means to implement DCV using CO2 concentration, including establishing CO2 maximum concentrations above ambient for each occupancy type. Standard 90.1 Addendum o • Requires that DCV controls and sensors meet the minimum requirements of Standard 62.1 (in applications where compliance with Standard 62.1 is not already mandated) • Requires that sensors and controllers be capable of and configured to maintain the maximum CO2 concentration prescribed by ASHRAE Standard 62.1 Addendum ab. Using these maximum concentration values in DCV logic will maximize energy savings. | Section 3 (modify) 6.4.3.8 (modify) | Energy Savings
14 | p | 2024-05-31 | This addendum makes updates to requirements for minimum outdoor air. Modify Section 6.4.3.4.2 as follows. 6.4.3.4.2 Shutoff Damper Controls. All outdoor air intake and exhaust systems shall be equipped with motorized dampers that will automatically shut when the systems or spaces served are not in use. Outdoor air and exhaust/relief dampers shall be capable of and configured to automatically shut off when HVAC systems are operated but HVAC zones served are not scheduled or indicated to be occupied by a device meeting the requirements of Sections 6.4.3.3.1, such as for during pre-occupancy building warm-up, cooldown, and setback, except when the supply of outdoor air reduces energy costs or when outdoor air must be supplied to meet code requirements the required minimum outdoor air rate. Modify Section 6.5.3.8 as follows. 6.5.3.8 Ventilation Design. 6.5.3.8.1 Ventilation for Acceptable Air Quality. The design minimum outdoor air rate to each HVAC zone and each HVAC system required minimum outdoor air rate is the larger of the minimum outdoor air rate or the minimum exhaust air rate required by Standard 62.1, Standard 62.2, Standard 170, or applicable codes or accreditation standards. Outdoor air ventilation systems shall comply with one of the following: a. Design minimum system outdoor air provided shall not exceed 135% of the required required minimum outdoor air rate rate by more than 30%. HVAC zones and HVAC systems with a design minimum outdoor air rate greater than 105% of the required minimum outdoor air rate shall include automatic zone flow control dampers or automatic outside air zone flow control dampers. b. Dampers, ductwork, and controls shall be provided that allow the system to supply no more than the required minimum outdoor air rate with a single set-point adjustment. c. The system includes exhaust air energy recovery complying with Section 6.5.6.1. Informative Note: This section does not limit outdoor air used for economizing in accordance with Section 6.5.1. 6.5.3.8.2 Ventilation for Disease Transmission Mitigation. Where ventilation is used to mitigate disease transmission to meet ASHRAE Standard 241 or ANSI/ASHRAE/ASHE Standard 170, the outdoor air component of the ventilation rate shall meet the limitation of Section 6.5.3.8.1. Informative Note: Other methods of mitigating disease transmission, such as cleaned recirculated air, are not limited by this standard. | Section3 (modify) 6.4.3.4.2 (modify) 6.5.1.1.3 (modify) 6.5.2.1 (modify) 6.5.2.3 (modify) 6.5.3.3 (modify) 6.5.3.8 (modify) 6.5.7.1 (modify) 11.5.2.2.6 (modify) 12.5.2 (modify) 13 (modify) C3.5.8 (modify) G3.2.2.4 (modify) G3.2.2.7.1 (modify) G3.2.3.13 and 14 (modify) G3.2.3.17 (modify) | Energy Savings
15 | q | 2024-03-14 | Addendum q adds pad-type (wetted media) adiabatic fluid coolers along with a minimum efficiency and the recently published CTI acceptance test code to Table 6.8.1-7, “Heat Rejection Equipment.” |  | Energy Savings
16 | r | 2024-05-31 | Addendum r modifies and clarifies core terminology within ANSI/ASHRAE/IES Standard 90.1, creating a distinction between the generic use of the word “floor” and the proposed revision of the defined term, “floor.” Floor, which is an element of the building’s thermal envelope, will become the term “envelope floor,” which better describes the intended application of the term. |  | Administrative
17 | s | 2024-07-24 | Addendum s splits the lighting power density (LPD) values and lighting control requirements from Table 9.5.1.2-1 into two new tables. The first table lists spaces with lighting controls and is placed in section 9.4. A second table lists LPD values for spaces and remain in section 9.5.2. This change makes clear that the lighting control requirements apply when using both the Building Area Method and the Space-by-Space Method. In the new LPD table, values are revised. The modified LPD values result from refining the Standard 90.1 lighting model and collaboration with IALD and IES. Since 2019, all fixture types in the model use LED sources. The revised values result from three major changes: updated lamp lumen deprecation values, revised process for determining luminaire dirt depreciation, and updated luminaire efficacy values. | 9.4.1 .1 (modify) 9.5 (modify) 9.5.2 (modify) Tables 9.4.1-1 and 9.4.1-2 (add) Tables 9.5.2.1-1 and 9.5.2.1-2 (replace) Table 9.5.2.2 (modify) | Energy Savings
18 | t | 2024-05-31 | Addendum t removes Section 9.5.2.3, “Control Factors.” Section 9.5.2.3 was added to ANSI/ASHRAE/IES Standard 90.1 in 2013 to allow for advanced lighting controls. Many of those advanced controls are now part of the standard. In 2013, inefficiencies with fluorescent dimming technology required more power than standard fluorescent ballasts to work with certain controls. The industry has shifted from fluorescent to LED technology. LED technology does not have the same electrical efficiencies. For these reasons, Section 9.5.2.3 is no longer necessary. |  | Energy Savings
19 | u | 2024-12-31 | Addendum u addresses issues that have been reported with the minimum 50% turndown airflow defined in Section 6.5.3.2(b). With the addition of occupied standby control as defined in Section 6.5.3.9, issues have been reported with variable-air-volume (VAV) systems that control space temperature by modulating airflow to the space (multizone VAV). The current minimum airflow requirements defined in Section 6.5.3.2 require a minimum turndown fan speed of 50%. Fifty percent is not acceptable for periods where the building occupancy is low and the ventilation airflow and required building airflow are significantly lower than the 50% minimum requirement. Fifty percent is well above the minimum design ventilation rates for typical buildings that use multizone VAV, and with occupied standby, the ventilation rates can be even lower when operating in ventilation-only mode. The “Minimum ANSI/ASHRAE Standard 62.1 Design Ventilation Rates” table shows minimum design ventilation rates for typical multizone VAV building applications. Systems with only a minimum 50% airflow turndown rate can result in cycling of equipment and poor control of the building VAV system and, in some cases, tripping of unit’s safety devices. To solve this problem, some applications have been forced to add a bypass duct (see the figure below) to allow air to recirculate and to keep the unit from tripping on safeties; however, this increases annualized fan power and product installation costs. Multizone VAV systems today are equipped with inverter fan speed control and are capable of much lower speeds and turndown than the required minimum 50%. Addendum u reduces the minimum airflow for multizone VAV systems where the space temperature is controlled by modulating airflow from 50% to 15%. In addition, the current power reduction requirement of 30% at 50% airflow is much higher than what is delivered by variable speed inverter driver fan systems. Based on this, the fan system power requirements will be changed from 30% at 50% airflow to 16% at 15% airflow. | 6.5.3.2.1 (modify) | Energy Savings
20 | v | 2024-05-31 | Addendum v to Standard 90.1 updates the reference annex climate zone data to that in the current Standard 169-2021. The data and tables in Standard 169-2021 have been completely revised and updated from Standard 169-2013. Standard 169-2021 includes data for 9237 weather station locations throughout the world, compared to 5564 locations in Standard 169-2013, for an increase of 3673. |  | Administrative
21 | w | 2024-11-05 | Addendum w reduces the decorative lighting allowance to reflect current LED technology and practices. More efficient lighting sources allow for a lower allowance. The decorative lighting allowance was first included in the 1999 edition of the standard and was 1.0 W/ft2. The value was reduced in 2016 to 0.75 W/ft2 and again in 2022 to 0.7 W/ft2. This addendum provides a fixed value of 0.50 W/ft2 for all spaces. | Table 9.5.2.2 (modify) | Energy Savings
22 | x | 2024-05-31 | Addendum x addresses the requirement for isolation zones in Section 6.4.3.3.4. It adds an exception to the requirement where ANSI/ASHRAE/ASHE Standard 170-2021, Ventilation of Health Care Facilities, or other standards require continuous airflow to maintain space pressure differential requirements. |  | Administrative
23 | y | 2024-12-31 | Addendum y modifies Section 6.5.6.1.1 to provide clear requirements for exhaust air energy recovery for nontransient dwelling units and add compliance path using CAN/CSA C439. | 3.2 (revise) 6.5.6.1 (revise) Table 6.5.6.1.2-1 (modify) Table 6.5.6.1.2-2 (modify) Section 13 (revise) | Energy Savings
24 | z | 2024-05-31 | Addendum z addresses the following: • An omitted exception in Section 9.2.2.2 that was identified in a recent official interpretation • Removing the exception in Section 9.5.2.2 from the text and placing it into Table 9.5.2.2 so that its placement does not confuse users of the standard |  | Energy Savings
25 | ab | 2025-05-09 | Addendum ab changes the names and definitions of the lighting zones to match new definitions/terms established by the Illuminating Engineering Society. The lighting power density (LPD) values change as follows: - Some areas now have a value for LZ0. This change is consistent with the new guidance by the lighting industry. - Many areas experienced a reduction of 15%. This reduction is a combination change in design practice (lamp lumen depreciation shifting from 0.85 to 0.90), increase in device efficacy, as well as a change in luminaire dirt depreciation. - A few areas reduced by 20% (the 15% explained above the second 5% from a realignment in design). - Dining areas reduced by 50%, this is a realignment in design. The LPD for dining areas LZ4 (dense urban) should be less than the LPD for interior dining | 9.1.1.1 (modify) 9.4.1.4 (modify) Table 9.5.3-1 (modify) Table 9.5.3-2 (modify) | Administrative
26 | ad | 2024-09-30 | Addendum ad simplifies the standard by deleting the terms “code official” and “building official” and replacing them with “authority having jurisdiction.” It also updates the definition of “authority having jurisdiction” to be inclusive of the deleted terms. |  | Energy Savings
27 | af | 2025-05-30 | Addendum af modifies Section 10.4.1, covering electric motor efficiency, to align with DOE 10 CFR 431. U.S. DOE published a Federal Register direct final rule on June 1, 2023, pertaining to energy conservation standards for electric motors. In this direct final rule, DOE is adopting new and amended standards for electric motors. Starting June 1, 2027, the efficiency of 100 to 250 hp (75 to 186 kW) NEMA Design A motor, NEMA Design B motor, and IEC Design N (including NE, NEY, or NY variants) motor, but excluding fire pump electric motors and air-over electric motors (manufactured alone or as a component of another piece of equipment), has been changed. DOE also has published the minimum efficiency of an air-over electric motor built in a standard frame size and specialized frame size of an air-over electric motor with a power rating from 1 to 20 hp. | Section 3 (modify) 10.4.1 (modify) Table 10.8-1 (modify) Table 10.8-7 (add new) Table 10.8-8 (add new) Table 10.8-9 (add new) | Energy Savings
28 | ag | 2024-10-31 | Addendum ag, initiated by a continuous maintenance proposal, improves the definition of “series energy recovery ratio (SERR)” by removing the specific dry-bulb condition at which it is rated to allow the term to be used for different conditions. The rated entering air conditions have been moved to Exception 7 to Section 6.5.6.1.2, which covers exhaust air energy requirements for other than nontransient dwelling units. |  | Energy Savings
29 | ah | 2024-12-31 | A recent proposal suggested the removal of the names of specific simulation programs from the standard. These names are no longer useful, because the modeling industry has expanded and matured and understands the available software. In addition, inconsistencies between these parallel sections were identified, and changes were made to make them more consistent. The sentences concerning how components are modeled were updated to read better and be self-consistent. |  | Administrative
30 | aj | 2025-04-30 | This independent substantive change is in response to comments. There are two changes: 1. The text in Section 6.5.6.4.1 has been modified to make it clear that supplemental heat can operate as long as 100% of the recovered heat is used at that moment. 2. A definition for thermodynamic heat recovery, which uses a refrigerant circuit for exhaust air energy recovery, has been added, and that method has been added as an option in Section 6.5.6.4.2 | 3.2 (modify) 6.5.6.1.2 (modify) 6.5.6.4 (modify) Table 6.5.6.4 (add) Table 12.5.1(12) (modify) Table G3.1(1) (modify) | Energy Savings
31 | ak | 2025-07-31 | Single zone HVAC system using electricity for heat, baseline HVAC must be a packaged heat pump. | Omitted due to publishing after May, 2025
32 | am | 2025-04-30 | Addendum am revies the fenestration prescriptive criteria in Tables 5.5-0 through 5.5-8. The assembly maximum U-factor has been reduced in CZ 5-7. | Table 5.5-0 - 5.5-8 (modify) Table 12.5.1 (modify) Appendix C3.6 (modify) | Energy Savings
33 | an | 2024-10-31 | Addendum an revises Section 9.5.1 Building Area Method lighting power density (LPD) values. These values are developed via a space-weighted average using Section 9.5.2 Space-by-Space Method individual LPD values. Addendum s, which received only one editorial comment, included the revised Space-by-Space LPD values. These values are directly based on Addendum s. The cost-effectiveness analysis was done during the development of Addendum s, and this is an alternate compliance pathway. | Table 9.5.1 (modify) | Administrative
34 | aq | 2025-05-09 | Addendum aq increases the required on-site rated capacity from 0.5 W/ft2 to 0.75 W/ft2. These changes are to ANSI/ASHRAE/IES Standard 90.1-2022 including Addendum k. This addendum fixes unit conversion errors in Table 10.5.1.3 and defines the units used in the equation for TREOFF, the total off-site renewable energy. The addendum also updates the reference to the Green-e standard for qualifying RECs to the latest version. |  | Administrative
35 | ar | 2025-03-11 | Addendum ar requires that an energy cost budget (ECB) and Appendix G analysis be conducted using actual utilities rates or supply contracts from utilities or energy suppliers versus average U.S. DOE Energy Information Administration (EIA) rates when available. Actual utility rate schedules often include demand charges that can significantly impact the annual energy cost of a project, especially projects incorporating load management energy efficiency measures. Note that the standard does not guarantee the prediction of actual building operational costs. | 3.2 (revise) 12.4.3.2 (revise) Table 12.5.1 (revise) G2.1 (revise) G2.4.2 (revise) Table G3.1 (revise) | Administrative
36 | as | 2025-04-30 | Addendum as substitutes a newly defined term, “expanded performance data,” for most locations in Standard 90.1 that previously referenced “performance curves.” |  | Energy Savings
37 | at | 2025-03-11 | Addendum at adds the necessary referencing language to utilize ASHRAE Standard 140-2023, including the acceptance ranges to be met, reporting requirements, and details necessary for testing to Standard 90.1 in the four sections that referenced it. This addendum also reduces redundancy in Standard 90.1 by citing Standard 140 only in Appendix G, which includes all the necessary details, and letting Section 12, Appendix C, and Appendix L simply reference the section in Appendix G related to Standard 140. The use of a simulation engine and a simplified interface for programs that comply with Appendices C and L have traditionally meant that only the simulation engine and not the entire program including user interface were tested according to Standard 140; this addendum makes that explicit. |  | Energy Savings
38 | au | 2024-10-31 | Addendum au aligns how automated shading and dynamic glazing are modeled in Section 12 with Normative Appendix G, not giving credit for manual shading, but allowing permanently installed automatically controlled shading devices and dynamic glazing to be modeled. Performance properties of automatically controlled shading devices must be determined in accordance with AERC 1 from the Attachments Energy Rating Council. At the same time, Addendum au cleans up italicized terms in both Section 12 and Normative Appendix G. |  | Energy Savings
39 | av | 2024-12-31 | Addendum av clarifies existing building envelope alteration provisions in Section 5.1.4 and improves upon similar updates to the 2024 IECC, Chapter 5, “Existing Buildings.” In some cases, the existing exceptions in Section 5.1.4 are exceptions; in other cases, they are requirements. The list of exceptions is incomplete or lacking appropriate triggers for when alteration requirements should or should not apply and to what degree. This addendum reformats the provisions of Section 5.1.4 to address alteration requirements, exceptions, triggers, and allowances to better accommodate alterations for various building thermal envelope assemblies while promoting energy efficiency improvements. It also seeks to provide flexibility in allowing deviation from the provisions for new construction by way of an “approved” design to accommodate existing building conditions that may sometimes inhibit full compliance with the envelope requirements for new construction (similar to the approach already used with roof replacements). |  | Energy Savings
40 | aw | 2024-10-31 | Addendum aw updates the calculation methods for steel-frame wall assemby U-factors by evaluating the available hot-box test data to derive a consistent linear thermal bridge Psi-factor for steel framing members. |  | Administrative
41 | ay | 2024-10-31 | Addendum ay clarifies the mass, steel frame, and wood frame wall base assemblies in Normative Appendix A and provides a means to determine the U-factor of a base wall assembly with an added layer of framing or furring with thermally-bridged cavity insulation. This assembly is a common application that does not comply with the definition of “continuous insulation.” But, the standard does not currently provide a means to determine an assembly U-factor for this condition (including the impact of the thermally-bridged exterior insulation). A method already exists for similar purpose in Section A3.1.3.2(b) for mass walls. It is updated in this addendum and applied similarly to steel-frame and wood-frame walls. |  | Energy Savings
42 | az | 2025-03-11 | Addendum az includes new definitions and Chapter 8 mandatory provisions for AC electric vehicle spaces. These new requirements add: a. Branch circuits serving EV spaces shall have a rated voltage of not less than 208 V. b. In buildings other than multifamily, branch circuits serving charging of EVs shall have conductors sized to deliver a continuous duty load of not less than 6.6 kVA to each EV space and circuit protection sized to serve the load. c. In buildings other than multifamily, electric vehicle supply equipment (EVSE) shall be capable of being controlled by a building management system or grid services aggregator. | 3 (revise) 3.3 (revise) 8.4.5. (revise) | Administrative
43 | bb | 2024-09-30 | Increasing the minimum efficiency of axial fan open-circuit cooling towers will save energy, and the new level will match the mandatory level in California Title 24. This efficiency increase is not expected to result in any meaningful market shift from water-cooled systems to alternative cooling solutions. This change will impact a relatively small segment of the market that is currently below the 42.1 gpm/hp efficiency level, increasing cost slightly for these selections. |  | Administrative
44 | bd | 2025-05-09 | Addendum bd revises the interior lighting control requirements in various sections, mainly Section 9.4.1.1 and Tables 9.4.1.1-1 and 9.4.1.1-2 with the following: - Various editorial changes and revisions to correct errors, - Change in nomenclature to “occupancy sensor reduction control” and “occupancy sensor shutoff control” in Sections 9.4.1.1(g) and 9.4.1.1(h) to be more specific about application of controls that accomplish the action and to be more consistent with the use of “occupancy sensor” as a defined term - Changes to various control requirements in Tables 9.4.1-1 and 9.4.1-2 to match typical design and application use, such as eliminating local controls and multilevel controls in spaces due to safety or where use is not common - The addition of auto reduction control to space types to increase energy efficiency by reducing lighting energy use and reducing ventilation where ventilation rates are permitted to go to zero in occupied standby mode - A new lighting control methodology for some health care facility spaces where lighting can be reduced during night hours to coincide with human lighting adaptation - Control of lighting in office areas larger than 300 ft2 (open offices) to be more clearly described in its own section - Change of the occupancy sensor time delay from 20 minutes to 15 minutes in base prescriptive requirements utilizing occupancy sensor technologies to regulate lighting. This provides an additional 2% to 5% lighting energy savings for spaces required to use occupancy sensor control without any additional costs. - Various changes to resolve efficiency loopholes and inconsistencies with design practice and lighting control common use | 6.5.3.9 (modify) 9.1.1.3.1 (modify) Table 9.2.2.2 (modify) 9.4.1 (modify) 9.4.1.2 (add) Table 9.4.2-2 (modify) 9.4.3.2 (modify) Table 9.4.1.1-1 and 9.4.1.1-2 (modify) Table 9.5.2.2 (modify) Tbale H-1 (modify) | Energy Savings
45 | be | 2025-05-30 | Addendum be updates Section 9, “Lighting” scope; exceptions in Section 9.3, “Simplified Building Method Compliance Path,” and exceptions in Section 9.4.1.1, “Interior Lighting Controls,” where lighting is designed to remain ON in support of building exit access. This addendum accomplishes the following: • Adds clarity to lighting power used for illumination that remains ON by this exception to lighting control shutoff requirements found in five locations of Section 9. • Reduces the exempt lighting power watts per square foot allowance from 0.02W/ft2 to 0.01W/ft2 across • the gross lighted floor area. • Defines the purpose and use of the exempt lighting power for exit access. • Improves alignment of the standard with terminology used by building codes. • Adds the defined term “exit access,” which is defined in U.S. building codes for interpretive simplicity and to support international use of the standard. | 3.2 (modify) 9.1.1.1 (modify) Tables 9.3.1-1, 9.3.1-2, and 9.3.1-3 (modify) 9.4.1.1 (modify) | Administrative
46 | bf | 2025-07-31 | Additional insulation to prescriptive code. | Omitted due to publishing after May, 2025
47 | bg | 2025-04-30 | Addendum bg makes clear that, where present, all layered board insulation shall be offset. Additionally, where that insulation is above a roof deck, it shall be installed in two layers where the joints are offset. A single layer is limited to the portion of a taper adjacent to a drain element. The cost of installing two layers of insulation instead of one is not significant and is common practice. |  | Administrative
48 | bh | 2025-04-30 | Addendum bh is a response to request from ASHRAE Standing Standard Project Committee (SSPC) 189.3 members to require unoccupied setback in hospital/healthcare spaces. The working committee selected high air change spaces in which ANSI/ASHRAE/ASHE Standard 170 permits unoccupied setback. | 6.4.3.3 (modify) 6.4.3.3.6 (add) | Administrative
49 | bl | 2025-04-30 | Addendum bl only makes changes to the following necessary items: - Removes “whirlpool” from the definition of “pool,” as this is a type of bathtub and not a pool or spa - Adds therapy as an activity that can performed in a pool to ensure therapy pools are covered - Clarifies that a portable electric spa (PES) is not a pool, providing a separate definition for PES that follows the U.S. Department of Energy (DOE) definition, adding to the definition that to qualify as a PES, they must also be tested to the ANSI/APSP/ICC-14 Standard or Appendix GG to 10 CFR Part 430 | 3.2 (modify) 7.4.5.2 (modify) | Energy Savings
50 | bo | 2025-05-16 | Fan Power Limits Addendum bo updates fan power limits in Section 6.5.3.1 based on updates to California Title 24-2022, and in consideration of the cost-effectiveness requirements used for Standard 90.1. The increase in stringency ranges is, on average, about 10%, though the amount varies by fan system type. A spreadsheet tool allows users to check compliance for each of three system types: single fan, supply/ return fan, or complex fan systems. In each worksheet, the user can enter fan system parameters and see how the resulting power allowance for the proposal compares against the two existing options in ASHRAE/ IES Standard 90.1-2022 (i.e., the motor nameplate method and the brake horsepower method). (Note: Users only need to modify the orange input cells.) Addendum bo solves many problems with the current requirements: • The present method limits fan shaft power and does not consider the actual electric input power. Further, it does not cover the efficiency of the fan transmission, motor, or variable-speed controller. Addendum bo provides requirements for fan system electrical input power. • The existing requirements are based on pressure losses for a large air handler (e.g., 3.5 in. of water for duct losses for a multizone system). Addendum bo provides requirements for small, medium, and large systems. • Fan power limits do not apply to alterations. Addendum bo adds scope alterations with additional fan power allowances to account for existing duct systems and adapter curbs. Reviewers should note that direct replacement of existing fans is exempted from this requirement. • New fan power allowances have been created for components that have become more common, including hot-gas reheat coils, water economizer coils, and series energy recovery. • Addendum bo recognizes the efficiency of using direct-drive instead of v-belt transmissions. • Any supply fan that does not move air through a source of heating or cooling. For example, large energy recovery ventilators are out of scope. The scope would now cover these products. • The existing language excludes fans that do not serve conditioned spaces. Addendum bo includes all fans serving interior spaces. • The existing language includes only fan systems where the fan nameplate horsepower totals more than 5 hp (3.7 kW). This excludes all fan systems up to approximately 5000 cfm (2400 L/s). The power threshold is reduced to 1 kW input power | 3.2 (modify) 6.1.4 (modify) 6.5.3.1 (modify) Tables to Section 6.5.3.1 (add new) 13 (modify) | Energy Savings
51 | bp | 2025-04-30 | Addendum bp removes the mechanical performance factors (MPFs) from the total system performance ratio (TSPR) calculation found in Section 6.6.2 of Standard 90.1. The stringency of TSPR remains unchanged. | 6.6.2 | Administrative
52 | br | 2025-05-09 | Addendum br provides an optional method to comply with the graphical display of the electrical energy monitoring requirement |  | Energy Savings
53 | bv | 2025-04-30 | Addendum bv updates Section 12. Section 12, “Energy Cost Budget,” includes equations to remove the fan power from the hypothetical baseline mechanical system. New efficiency metrics were introduced in the Section 6 mechanical equipment tables where SEER and HSPF values were updated to SEER2 and HSPF2 values. These equations apply to baseline Systems 3, 4, 9, and 11 when the systems are under 65,000 Btu/h. The Department of Energy issued EERE–2014–BT–STD– 0048, which identifies the translation of SEER to SEER2 and HSPF to HSPF2 equivalency. The single-package AC and HP had a SEER of 14 with a new, SEER2 rating of 13.4. The single-package heat-pump HSPF of 8.0 changed to an HSPF2 of 6.7. Lacking further industry data, this proposal uses the ratio of the old-to-new metrics to update the Section 12 equations. | 12.5.2 (modify) | Energy Savings
54 | bw | 2025-05-30 | This addendum adds a provision for buildings required to have a DDC system to also provide a graphical display for monitored non-electrical energy use. This addendum is not anticipated to add cost because the DDC must already be installed within the building to trigger this requirement. | 10.4.7.2 (modify) | Administrative
55 | by | 2025-05-30 | As a result of new humidity set-point requirements in ANSI/ASHRAE/ASHE Standard 170-2021, hospitals generally no longer qualify for the Standard 90.1 economizer exception #4 to Section 6.5.1, which is based on zone dew point. Addendum by adds an exception to the economizer requirement for hospital buildings that use a heat recovery chiller for space heating. Using an economizer in these systems severely limits the potential for energy recovery, since the chiller is often off during economizer operation. To evaluate the impact of this exception, a simulation analysis was conducted with the PNNL Hospital prototype model in five climates with and without air economizers. The case without an economizer consistently uses less energy than the case with an economizer. The energy cost impact is shown in Table 1 without the social cost of carbon and in Table 2 with utility rates that account for the social cost of carbon. | Exception to Section 6.5.1 (add new) | Energy Savings
56 | bz | 2025-07-31 | Horticulture lighting. | Omitted due to publishing after May, 2025
57 | ca | 2023-07-25 | Technologies have been developed that allow active communication and interaction between buildings and building systems and their utility sources and energy grids. This interactive link offers opportunities for building energy designs to further energy saving goals. Addendum ca expands the scope of Standard 90.1 to allow the use of effective design strategies for buildings when interacting with their sources of energy. Future changes to the standard would include criteria for buildings to utilize these interactive design strategies. |  | Energy Savings
58 | cb | 2025-05-30 | Addendum cb updates the graphic associated with Section 10 of the standard. Updating the graphic revealed a need to replace the phrase “other equipment” with one less ambiguous. The compliance path in Section 10 is updated to better reflect what the graphic illustrates, following similar methods used in Section 6 that provide a better description of the standard’s intent. The list of mandatory sections is converted from sentence format to a list format. Changes noted herein have no cost impact. | 10.1 (modify) 10.2 (revise) 10.9 (revise) | Energy Savings
59 | cd | 2025-05-30 | Addendum cd edits are the result of the Format and Compliance team’s review of initialisms and acronyms. Note, if an initialism or acronym only exists in formula and is described in the formula, that term is excluded from the list unless used in more than one location in the standard. | Section 3.3 Abbreviations and Acronyms | Energy Savings
60 | ce | 2025-05-30 | The intent of the original language related to rotating the baseline model four times was to provide an incentive for good orientation of a building’s facades with large window areas. Along with this was the concept that rotating a building is generally simple to do in most simulation programs by simply changing the overall orientation of the building and rerunning the simulation. The existing language has been interpreted by some people to mean that all the rules of creating a baseline are repeated for each rotation—essentially exercising the Appendix G rules four times—but that creates additional work and may be counter to the original intent of rewarding good orientation. Most modelers follow this original intent already, and now Addendum ce includes changes to more clearly reflect the intended language. Of four software program vendors that were contacted that provide some automation for Appendix G, three of them were supportive of the proposed clarification. Similar changes were made in Section 12 and Appendix C. In addition, a change to how the shading should be performed to provide incentives for buildings intending to shade themselves has been added. | Table 12.5.1 (modify) C3.6 (revise) Table G3.1 (revise) | Energy Savings
61 | cf | 2025-05-30 | Section 12, “Energy Cost Budget Method,” and Normative Appendix G, “Performance Rating Method,” are two available whole-building performance compliance options. Each option has different limitations and advantages. Two new informative notes are proposed and summarized below. 1. Addresses a CMP and helps the practitioner avoid spending time evaluating PRM under difficult applications. 2. Highlights PRM advantages to achieve positive compliance outcome | 4.2.1.1 (added informative note for New Buildings) | Administrative
62 | cg | 2025-05-30 | App G Performance Path calculation for improved performance.
63 | ch | 2025-05-30 | Addendum aw to ANSI/ASHRAE/IES Standard 90.1-2022 includes an improved methodology (new equation) to determine U-factors for steel frame wall assemblies. Recently, it was discovered that new Table A3.3.3.1 of Addendum aw had precalculated U-factor values that did not agree with the new equation. This was traced to a simple formulaic error in the spreadsheet for the base wall assembly that propagated to all the calculated U-factors for Table A3.3.3.1 resulting in U-factors that were greater than intended by the new equation. This addendum corrects only the U-factor values without changing the format of Table A3.3.3.1 or the text and equation that was correctly addressed in Addendum aw | Delete existing Table A3.3.3.1 and replace with new Table A3.3.3.1 | Energy Savings
64 | ck | 2025-07-31 | Improved lighting performance. | Omitted due to publishing after May, 2025
65 | cv | 2023-02-28 | Addendum cv makes the following changes: a. Updates existing ASHRAE Standard 90.1-2019 ISMRE and ISCOP standards to ISMRE2 and ISCOP2 standards using the crosswalk analysis proposed by DOE in the February 1, 2022, notice of proposed rule for eight equipment classes. b. For the four equipment classes covered by Standard 90.1, but not considered by DOE, this addendum updates existing Standard 90.1-2019 ISMRE and ISCOP standards to ISMRE2 and ISCOP2 standards based on an industry analysis. Four of these equipment classes will be combined into two. c. Adds AHRI Standard 920-2020 to Section 12, “Normative References.” |  | Energy Savings
66 | cw | 2023-08-30 | Addendum cw was composed in response to a change in the IBC 2021 identified by the IALD. The IBC 2021 added a requirement that along exit access stairways, the illumination level must be a minimum of 10 fc (108 lux) at the walking surface when the stairway is in use. Prior to this, the illumination level for means of egress was required to be at least 1 fc (11 lux) at the walking surface. This is a potential ten-fold increase in lighting in exit stairways. To maintain current energy efficiency levels and limit trading of this power to nonstair spaces, Addendum cw creates a new additional lighting power allowance for exit access stairways. The additional power is limited to this space only and prevents the trading of power to other spaces. |  | Energy Savings